## Test Matrix
Index | Baseline Model (BRS) | Baseline Model (E+) | Climate | SAT Reset Type | Annual Kbtu/sf Total (EnergyPlus) | Annual Kbtu/sf Electric (EnergyPlus) | Annual kBtu/sf Gas (EnergyPlus) | Electricity Total Energy Savings (EnergyPlus) | Natural Gas Total Energy Savings (EnergyPlus) | Total Savings (EnergyPlus) | Fan kBtu/sf (EnergyPlus) | Cooling, inc. towers kBtu/sf (EnergyPlus) | Pump kBtu/sf (EnergyPlus) | Fan Savings (EnergyPlus) | Cooling, in. towers Savings (EnergyPlus) | Pump Savings (EnergyPlus) | Unmet Thermostat (EnergyPlus) (%) | Electricity Savings (EnergyPlus) (%) | Natural Gas Savings (EnergyPlus) (%) | TotalSavings (EnergyPlus) (%) | Annual Kbtu/sf Total (BRS) | Annual Kbtu/sf Electric (BRS) | Annual kBtu/sf Gas (BRS) | Electricity Total Energy Savings (BRS) | Natural Gas Total Energy Savings (BRS) | Total Savings (BRS) | Fan kBtu/sf (BRS) | Cooling, inc. towers kBtu/sf (BRS) | Pump kBtu/sf (BRS) | Fan Savings (BRS) | Cooling, in. towers Savings (BRS) | Pump Savings (BRS) | Unmet Thermostat (BRS) (%) | Electricity Savings (%) | Natural Gas Savings (%) | Total Savings (%)
B1 | 8-Zone Comissioned | 8-Zone Commissioned | New York | Baseline | 47.6791 | 37.7554 | 9.9238 |  |  |  | 5.5946 | 6.912 | 3.1495 |  |  |  | 18.22% |  |  |  | 49.08 | 33.51 | 15.57 |  |  |  | 4.44 | 5.43 | 1.51 |  |  |  | 6%
B2 | 8-Zone Comissioned | 8-Zone Commissioned | Houston | Baseline | 49.035 | 46.9038 | 2.1313 |  |  |  | 6.5343 | 13.2154 | 5.0549 |  |  |  | 24.86% |  |  |  | 47.2 | 40.25 | 6.95 |  |  |  | 4.81 | 11.01 | 2.29 |  |  |  | 1.8%
B3 | 8-Zone Comissioned | 8-Zone Commissioned | Minneapolis | Baseline | 56.8619 | 36.5493 | 20.3127 |  |  |  | 6.2008 | 5.7273 | 2.5219 |  |  |  | 19.86% |  |  |  | 63.0957 | 32.3248 | 30.7709 |  |  |  | 4.744 | 4.1132 | 1.3364 |  |  |  | 1.882%
B4 | 8-Zone Comissioned | 8-Zone Commissioned | Seattle | Baseline | 39.1119 | 32.7141 | 6.3978 |  |  |  | 4.7806 | 3.128 | 2.7063 |  |  |  | 15.56% |  |  |  | 41.22 | 28.85 | 12.37 |  |  |  | 3.39 | 2.18 | 1.15 |  |  |  | 4.9%
B5 | N/A | 15-Zone Commissioned | New York | Baseline | 49.5943 | 38.1363 | 11.458 |  |  |  | 5.1934 | 7.0221 | 3.2615 |  |  |  | 9.664%
B6 | N/A | 25-Zone Commissioned | New York | Baseline | 48.708 | 36.1323 | 12.5757 |  |  |  | 4.9661 | 6.5045 | 3.0052 |  |  |  | 11.3%
B7 | 8-Zone Faults Low | 8-Zone Faults Low | New York | Baseline | 53.6691 | 40.0018 | 13.6672 |  |  |  | 7.3478 | 7.4502 | 3.1047 |  |  |  | 18.19% |  |  |  | 52.11 | 34.58 | 17.53 |  |  |  | 5.2 | 5.73 | 1.52 |  |  |  | 6.7%
B8 | 8-Zone FaultsModerate | N/A | New York | Baseline | [16 empty] | 55.18 | 34.53 | 20.65 |  |  |  | 4.63 | 6.16 | 1.61 |  |  |  | 7.9%
B9 | N/A | 15-Zone FaultsLow | New York | Baseline | 52.7964 | 39.2734 | 13.523 |  |  |  | 6.0075 | 7.3462 | 3.2604 |  |  |  | 9.892%
B10 | N/A | 25-Zone FaultsLow | New York | Baseline | 49.9017 | 36.1904 | 13.7113 |  |  |  | 5.5006 | 6.2969 | 2.7364 |  |  |  | 12.56%
1 | 8-Zone Comissioned | 8-Zone Commissioned | New York | ASHRAE Guideline 36 | 45.2083 | 37.2812 | 7.9271 | 0.9946% | 4.188% | 5.182% | 5.667 | 6.6618 | 2.8532 | -0.1518% | 0.5248% | 0.6216% | 15.13% | 1.256% | 20.12% | 5.182% | 46.85 | 33.99 | 12.86 | -0.978% | 5.522% | 4.544% | 5.76 | 4.86 | 1.24 | -2.689% | 1.161% | 0.5501% | 10.1% | -1.43% | 17.38% | 4.53%
2 | 8-Zone Comissioned | 8-Zone Commissioned | Houston | ASHRAE Guideline 36 | 47.9696 | 46.3549 | 1.6148 | 1.119% | 1.053% | 2.173% | 6.4526 | 12.9302 | 4.8729 | 0.1666% | 0.5816% | 0.3712% | 20.97% | 1.17% | 24.23% | 2.173% | 44.75 | 40.15 | 4.6 | 0.2119% | 4.979% | 5.191% | 5.43 | 10.5 | 2.08 | -1.314% | 1.081% | 0.4449% | 3.7% | 0.23% | 33.82% | 5.17%
3 | 8-Zone Comissioned | 8-Zone Commissioned | Minneapolis | ASHRAE Guideline 36 | 53.9248 | 36.11 | 17.8148 | 0.7725% | 4.393% | 5.165% | 6.0408 | 5.5968 | 2.3732 | 0.2814% | 0.2294% | 0.2617% | 13.92% | 1.202% | 12.3% | 5.165% | 62.3758 | 33.1556 | 29.2201 | -1.317% | 2.458% | 1.141% | 6.0581 | 3.7842 | 1.1822 | -2.083% | 0.5215% | 0.2445% | 7.73% | -2.57% | 5.04% | 1.141%
4 | 8-Zone Comissioned | 8-Zone Commissioned | Seattle | ASHRAE Guideline 36 | 35.5852 | 31.1849 | 4.4003 | 3.91% | 5.107% | 9.017% | 4.8856 | 2.4005 | 1.7997 | -0.2683% | 1.86% | 2.318% | 9.265% | 4.674% | 31.22% | 9.017% | 37.53 | 29.19 | 8.34 | -0.8248% | 9.777% | 8.952% | 5.36 | 1.11 | 0.58 | -4.779% | 2.596% | 1.383% | 12% | -1.16% | 32.53% | 8.94%
5 | 8-Zone Comissioned | 8-Zone Commissioned | New York | OAT Linear | 45.0913 | 37.5545 | 7.5368 | 0.4213% | 5.006% | 5.428% | 5.8925 | 6.6812 | 2.8816 | -0.6248% | 0.4841% | 0.562% | 20.27% | 0.532% | 24.05% | 5.428% | 46.96 | 33.62 | 13.34 | -0.2241% | 4.544% | 4.319% | 5.11 | 5.08 | 1.3 | -1.365% | 0.7131% | 0.4279% | 7.5% | -0.33% | 14.34% | 4.33%
6 | 8-Zone Comissioned | 8-Zone Commissioned | Houston | OAT Linear | 48.4359 | 46.8445 | 1.5915 | 0.1209% | 1.101% | 1.222% | 6.746 | 13.0178 | 4.9815 | -0.4317% | 0.4028% | 0.1498% | 23.24% | 0.1264% | 25.33% | 1.222% | 45.04 | 39.68 | 5.36 | 1.208% | 3.369% | 4.576% | 4.69 | 10.76 | 2.09 | 0.2542% | 0.5297% | 0.4237% | 2.5% | 1.41% | 22.85% | 4.57%
7 | 8-Zone Comissioned | 8-Zone Commissioned | Minneapolis | OAT Linear | 53.4018 | 36.0635 | 17.3384 | 0.8543% | 5.231% | 6.085% | 6.2461 | 5.4395 | 2.2787 | -0.07953% | 0.5061% | 0.4278% | 23.46% | 1.329% | 14.64% | 6.085% | 62.2724 | 33.0189 | 29.2535 | -1.1% | 2.405% | 1.305% | 5.7155 | 3.943 | 1.2292 | -1.54% | 0.2698% | 0.17% | 6.451% | -2.147% | 4.931% | 1.305%
8 | 8-Zone Comissioned | 8-Zone Commissioned | Seattle | OAT Linear | 34.9348 | 31.0227 | 3.9121 | 4.324% | 6.355% | 10.68% | 5.1104 | 2.0832 | 1.7299 | -0.8432% | 2.671% | 2.497% | 17.08% | 5.17% | 38.85% | 10.68% | 37.76 | 28.69 | 9.07 | 0.3882% | 8.006% | 8.394% | 4.46 | 1.38 | 0.72 | -2.596% | 1.941% | 1.043% | 7.7% | 0.57% | 26.67% | 8.4%
9 | 8-Zone Comissioned | 8-Zone Commissioned | New York | RAT Linear | 45.7792 | 37.4059 | 8.3733 | 0.733% | 3.252% | 3.985% | 5.6425 | 6.5638 | 3.1004 | -0.1004% | 0.7304% | 0.1031% | 13.8% | 0.9257% | 15.62% | 3.985% | 47.57 | 33.58 | 13.99 | -0.1426% | 3.219% | 3.077% | 4.98 | 5.11 | 1.36 | -1.1% | 0.652% | 0.3056% | 6.1% | -0.19% | 10.15% | 3.09%
10 | 8-Zone Comissioned | 8-Zone Commissioned | Houston | RAT Linear | 47.6691 | 46.11 | 1.559 | 1.619% | 1.167% | 2.786% | 6.7061 | 12.3115 | 4.9932 | -0.3504% | 1.843% | 0.1259% | 22.44% | 1.692% | 26.85% | 2.786% | 45.74 | 40.36 | 5.38 | -0.2331% | 3.326% | 3.093% | 5.39 | 10.69 | 2.15 | -1.229% | 0.678% | 0.2966% | 3.1% | -0.3% | 22.56% | 3.07%
11 | 8-Zone Comissioned | 8-Zone Commissioned | Minneapolis | RAT Linear | 54.05 | 35.9404 | 18.1096 | 1.071% | 3.874% | 4.945% | 5.932 | 5.4454 | 2.4638 | 0.4728% | 0.4957% | 0.1023% | 12.38% | 1.666% | 10.85% | 4.945% | 62.5489 | 32.5097 | 30.0392 | -0.2932% | 1.16% | 0.8665% | 5.1725 | 3.9482 | 1.2579 | -0.6792% | 0.2615% | 0.1245% | 2.942% | -0.5722% | 2.378% | 0.8665%
12 | 8-Zone Comissioned | 8-Zone Commissioned | Seattle | RAT Linear | 35.9914 | 30.94 | 5.0514 | 4.536% | 3.443% | 7.978% | 4.3117 | 2.4351 | 2.0941 | 1.199% | 1.771% | 1.565% | 7.037% | 5.423% | 21.05% | 7.978% | 38.35 | 28.52 | 9.83 | 0.8006% | 6.162% | 6.963% | 4.02 | 1.55 | 0.82 | -1.528% | 1.528% | 0.8006% | 5.5% | 1.14% | 20.49% | 6.95%
13 | 8-Zone Comissioned | 8-Zone Commissioned | New York | RAT "Bad Reset" Linear | 44.9346 | 37.6112 | 7.3233 | 0.3023% | 5.454% | 5.756% | 6.7188 | 5.8461 | 2.9471 | -2.358% | 2.236% | 0.4245% | 26.79% | 0.3817% | 26.2% | 5.756% | 48.94 | 36.44 | 12.5 | -5.97% | 6.255% | 0.2852% | 8.36 | 4.72 | 1.23 | -7.987% | 1.447% | 0.5705% | 20.4% | -8.74% | 19.73% | 0.29%
14 | 8-Zone Comissioned | 8-Zone Commissioned | Houston | RAT "Bad Reset" Linear | 47.5607 | 46.5808 | 0.97992 | 0.6587% | 2.348% | 3.007% | 7.6441 | 11.6746 | 5.1629 | -2.263% | 3.142% | -0.2202% | 34.37% | 0.6886% | 54.02% | 3.007% | 49.03 | 45.03 | 4 | -10.13% | 6.25% | -3.877% | 10.37 | 10.45 | 2.07 | -11.78% | 1.186% | 0.4661% | 21.1% | -11.88% | 42.43% | -3.89%
15 | 8-Zone Comissioned | 8-Zone Commissioned | Minneapolis | RAT "Bad Reset" Linear | 53.7503 | 36.4885 | 17.2617 | 0.1068% | 5.366% | 5.472% | 6.9706 | 4.9816 | 2.4372 | -1.354% | 1.311% | 0.1491% | 24.74% | 0.1661% | 15.02% | 5.472% | 64.3126 | 35.4759 | 28.8366 | -4.994% | 3.066% | -1.929% | 8.3355 | 3.8237 | 1.1856 | -5.692% | 0.4589% | 0.2391% | 16.68% | -9.749% | 6.286% | -1.929%
16 | 8-Zone Comissioned | 8-Zone Commissioned | Seattle | RAT "Bad Reset" Linear | 34.6328 | 30.918 | 3.7148 | 4.592% | 6.86% | 11.45% | 5.795 | 1.5575 | 1.4664 | -2.594% | 4.015% | 3.17% | 22.52% | 5.49% | 41.94% | 11.45% | 38.17 | 30.15 | 8.02 | -3.154% | 10.55% | 7.399% | 6.72 | 0.84 | 0.46 | -8.079% | 3.251% | 1.674% | 17.9% | -4.5% | 35.18% | 7.4%
17 | 8-Zone Comissioned | 8-Zone Commissioned | New York | Max Zn Damper T&R | 45.3649 | 36.6143 | 8.7505 | 2.393% | 2.461% | 4.854% | 5.461 | 5.9178 | 3.1364 | 0.2803% | 2.085% | 0.02753% | 10.12% | 3.022% | 11.82% | 4.854% | 48.34 | 33.68 | 14.66 | -0.3464% | 1.854% | 1.508% | 5.07 | 5.01 | 1.46 | -1.284% | 0.8557% | 0.1019% | 6.5% | -0.5% | 5.85% | 1.51%
18 | 8-Zone Comissioned | 8-Zone Commissioned | Houston | Max Zn Damper T&R | 46.3792 | 45.0374 | 1.3417 | 3.806% | 1.61% | 5.416% | 6.0351 | 11.6719 | 5.2313 | 1.018% | 3.148% | -0.3596% | 8.681% | 3.979% | 37.04% | 5.416% | 46.01 | 40.53 | 5.48 | -0.5932% | 3.114% | 2.521% | 5.97 | 10.14 | 2.29 | -2.458% | 1.843% | 0% | 4% | -0.7% | 21.11% | 2.51%
19 | 8-Zone Comissioned | 8-Zone Commissioned | Minneapolis | Max Zn Damper T&R | 54.1818 | 35.5873 | 18.5945 | 1.692% | 3.022% | 4.713% | 6.0739 | 4.8526 | 2.5616 | 0.2233% | 1.538% | -0.06977% | 14.18% | 2.632% | 8.459% | 4.713% | 63.3369 | 32.6376 | 30.6992 | -0.4959% | 0.1136% | -0.3823% | 5.2689 | 3.93 | 1.3056 | -0.8319% | 0.2903% | 0.04896% | 2.686% | -0.97% | 0.23% | -0.38%
20 | 8-Zone Comissioned | 8-Zone Commissioned | Seattle | Max Zn Damper T&R | 36.3088 | 30.9606 | 5.3482 | 4.483% | 2.684% | 7.167% | 4.6214 | 2.2404 | 1.9996 | 0.4071% | 2.269% | 1.807% | 7.384% | 5.36% | 16.41% | 7.167% | 39.16 | 28.54 | 10.62 | 0.7521% | 4.246% | 4.998% | 3.75 | 1.75 | 0.92 | -0.8734% | 1.043% | 0.558% | 5.7% | 1.07% | 14.14% | 4.99%
21 | 8-Zone Comissioned | 8-Zone Commissioned | New York | Avg Zn Damper Linear | 44.5164 | 36.588 | 7.9284 | 2.448% | 4.185% | 6.633% | 5.6348 | 5.8025 | 3.0515 | -0.0842% | 2.327% | 0.2055% | 7.228% | 3.092% | 20.11% | 6.633% | 48.1 | 34.58 | 13.52 | -2.18% | 4.177% | 1.997% | 6.27 | 4.85 | 1.32 | -3.729% | 1.182% | 0.3871% | 10.2% | -3.17% | 13.18% | 2.02%
22 | 8-Zone Comissioned | 8-Zone Commissioned | Houston | Avg Zn Damper Linear | 46.3438 | 45.1426 | 1.2012 | 3.592% | 1.897% | 5.488% | 6.4468 | 11.4179 | 5.1786 | 0.1784% | 3.666% | -0.2523% | 11.23% | 3.755% | 43.64% | 5.488% | 46.98 | 42.25 | 4.73 | -4.237% | 4.703% | 0.4661% | 7.63 | 10.28 | 2.21 | -5.975% | 1.547% | 0.1695% | 7.5% | -4.99% | 31.96% | 0.45%
23 | 8-Zone Comissioned | 8-Zone Commissioned | Minneapolis | Avg Zn Damper Linear | 53.2686 | 35.3713 | 17.8974 | 2.072% | 4.248% | 6.319% | 5.9622 | 4.8113 | 2.4986 | 0.4197% | 1.611% | 0.04103% | 7.008% | 3.223% | 11.89% | 6.319% | 63.1396 | 33.5984 | 29.5412 | -2.019% | 1.949% | -0.06961% | 6.3315 | 3.8991 | 1.2367 | -2.516% | 0.3394% | 0.1582% | 5.885% | -3.94% | 3.996% | -0.06961%
24 | 8-Zone Comissioned | 8-Zone Commissioned | Seattle | Avg Zn Damper Linear | 34.8198 | 30.5135 | 4.3063 | 5.626% | 5.347% | 10.97% | 4.9475 | 1.813 | 1.6538 | -0.4267% | 3.362% | 2.691% | 5.677% | 6.727% | 32.69% | 10.97% | 38.14 | 28.8 | 9.34 | 0.1213% | 7.351% | 7.472% | 5 | 1.1 | 0.57 | -3.906% | 2.62% | 1.407% | 10.7% | 0.17% | 24.48% | 7.46%
25 | 8-Zone Comissioned | 8-Zone Commissioned | New York | Zn Cooling − Zn Heating Linear | 44.5973 | 36.7891 | 7.8082 | 2.027% | 4.437% | 6.464% | 5.6742 | 5.9238 | 3.092 | -0.1668% | 2.073% | 0.1207% | 10.73% | 2.559% | 21.32% | 6.464% | 47.17 | 33.85 | 13.32 | -0.6927% | 4.584% | 3.892% | 4.98 | 5.37 | 1.37 | -1.1% | 0.1222% | 0.2852% | 7.6% | -0.99% | 14.46% | 3.91%
26 | 8-Zone Comissioned | 8-Zone Commissioned | Houston | Zn Cooling − Zn Heating Linear | 46.4405 | 45.2732 | 1.1673 | 3.325% | 1.966% | 5.291% | 6.5349 | 11.4395 | 5.1996 | -0.001101% | 3.622% | -0.2951% | 15.95% | 3.476% | 45.23% | 5.291% | 45.04 | 40.32 | 4.72 | -0.1483% | 4.725% | 4.576% | 5.02 | 10.98 | 2.18 | -0.4449% | 0.06356% | 0.2331% | 3.2% | -0.18% | 32.05% | 4.57%
27 | 8-Zone Comissioned | 8-Zone Commissioned | Minneapolis | Zn Cooling − Zn Heating Linear | 53.2254 | 35.6233 | 17.6021 | 1.628% | 4.767% | 6.395% | 6.0785 | 4.8952 | 2.5504 | 0.2152% | 1.463% | -0.05008% | 10.87% | 2.533% | 13.34% | 6.395% | 62.3148 | 32.759 | 29.5558 | -0.6882% | 1.926% | 1.238% | 5.2265 | 4.121 | 1.2803 | -0.7648% | -0.01239% | 0.08898% | 5.007% | -1.343% | 3.949% | 1.238%
28 | 8-Zone Comissioned | 8-Zone Commissioned | Seattle | Zn Cooling − Zn Heating Linear | 34.5687 | 30.2158 | 4.3529 | 6.388% | 5.228% | 11.62% | 4.4369 | 1.9723 | 1.7074 | 0.8787% | 2.955% | 2.554% | 3.374% | 7.637% | 31.96% | 11.62% | 37.47 | 28.47 | 9 | 0.9219% | 8.176% | 9.098% | 4.25 | 1.39 | 0.71 | -2.086% | 1.917% | 1.067% | 7.7% | 1.31% | 27.25% | 9.1%
29 | 8-Zone Comissioned | 8-Zone Commissioned | New York | Zn Cooling − Zn Heating T&R | 45.0153 | 36.9294 | 8.0859 | 1.732% | 3.855% | 5.587% | 5.5247 | 6.1024 | 3.2031 | 0.1467% | 1.698% | -0.1124% | 10.13% | 2.188% | 18.52% | 5.587% | 47.34 | 34.3 | 13.04 | -1.61% | 5.155% | 3.545% | 5.77 | 5.06 | 1.33 | -2.71% | 0.7539% | 0.3667% | 10.5% | -2.34% | 16.24% | 3.56%
30 | 8-Zone Comissioned | 8-Zone Commissioned | Houston | Zn Cooling − Zn Heating T&R | 46.7502 | 45.4617 | 1.2884 | 2.941% | 1.719% | 4.66% | 6.3885 | 11.6798 | 5.2943 | 0.2974% | 3.132% | -0.4882% | 15.19% | 3.074% | 39.55% | 4.66% | 45.28 | 40.75 | 4.53 | -1.059% | 5.127% | 4.068% | 6.01 | 10.44 | 2.16 | -2.542% | 1.208% | 0.2754% | 5.8% | -1.26% | 34.74% | 4.04%
31 | 8-Zone Comissioned | 8-Zone Commissioned | Minneapolis | Zn Cooling − Zn Heating T&R | 53.4475 | 35.4459 | 18.0015 | 1.94% | 4.064% | 6.005% | 5.7424 | 5.0114 | 2.593 | 0.8062% | 1.259% | -0.125% | 8.738% | 3.019% | 11.38% | 6.005% | 62.7435 | 33.3918 | 29.3517 | -1.691% | 2.249% | 0.5582% | 6.0177 | 3.99 | 1.2498 | -2.019% | 0.1952% | 0.1373% | 8.2% | -3.3% | 4.61% | 0.56%
32 | 8-Zone Comissioned | 8-Zone Commissioned | Seattle | Zn Cooling − Zn Heating T&R | 35.3161 | 30.6369 | 4.6791 | 5.311% | 4.394% | 9.705% | 4.2634 | 2.336 | 1.9383 | 1.323% | 2.025% | 1.963% | 2.905% | 6.349% | 26.86% | 9.705% | 37.59 | 28.87 | 8.72 | -0.04852% | 8.855% | 8.806% | 4.54 | 1.44 | 0.76 | -2.79% | 1.795% | 0.9461% | 8.6% | -0.08% | 29.46% | 8.78%
33 | 8-Zone Comissioned | 8-Zone Commissioned | New York | Zn Heating Linear | 46.7681 | 37.3373 | 9.4308 | 0.8768% | 1.034% | 1.911% | 5.3825 | 6.7138 | 3.1418 | 0.4449% | 0.4157% | 0.01616% | 13% | 1.107% | 4.967% | 1.911% | 47 | 33.92 | 13.08 | -0.8354% | 5.073% | 4.238% | 5.43 | 5.1 | 1.25 | -2.017% | 0.6724% | 0.5297% | 9.3% | -1.21% | 16.02% | 4.25%
34 | 8-Zone Comissioned | 8-Zone Commissioned | Houston | Zn Heating Linear | 47.6068 | 45.9537 | 1.6531 | 1.938% | 0.9752% | 2.913% | 6.7638 | 12.1667 | 4.9239 | -0.4681% | 2.139% | 0.2671% | 25.64% | 2.026% | 22.44% | 2.913% | 44.89 | 40.37 | 4.52 | -0.2542% | 5.148% | 4.894% | 5.38 | 10.81 | 2.05 | -1.208% | 0.4237% | 0.5085% | 4.7% | -0.32% | 34.9% | 4.87%
35 | 8-Zone Comissioned | 8-Zone Commissioned | Minneapolis | Zn Heating Linear | 55.586 | 35.8273 | 19.7587 | 1.27% | 0.9743% | 2.244% | 5.714 | 5.5446 | 2.4695 | 0.8563% | 0.3212% | 0.09215% | 11.86% | 1.975% | 2.727% | 2.244% | 62.633 | 33.1662 | 29.4669 | -1.334% | 2.067% | 0.7333% | 5.7611 | 4.0354 | 1.2385 | -1.612% | 0.1234% | 0.1552% | 7.2% | -2.603% | 4.238% | 0.7333%
36 | 8-Zone Comissioned | 8-Zone Commissioned | Seattle | Zn Heating Linear | 37.1829 | 31.5535 | 5.6294 | 2.967% | 1.965% | 4.932% | 4.316 | 2.8347 | 2.3037 | 1.188% | 0.7499% | 1.029% | 8.403% | 3.548% | 12.01% | 4.932% | 37.32 | 28.77 | 8.55 | 0.1941% | 9.267% | 9.461% | 4.68 | 1.29 | 0.66 | -3.13% | 2.159% | 1.189% | 9.3% | 0.28% | 30.9% | 9.47%
37 | 8-Zone Comissioned | 8-Zone Commissioned | New York | Zn Cooling Linear | 44.4692 | 37.0105 | 7.4587 | 1.562% | 5.17% | 6.732% | 6.2763 | 5.6688 | 2.9662 | -1.43% | 2.607% | 0.3845% | 20.26% | 1.973% | 24.84% | 6.732% | 47.41 | 33.97 | 13.44 | -0.9372% | 4.34% | 3.403% | 5.1 | 5.36 | 1.37 | -1.345% | 0.1426% | 0.2852% | 8% | -1.35% | 13.67% | 3.41%
38 | 8-Zone Comissioned | 8-Zone Commissioned | Houston | Zn Cooling Linear | 46.7745 | 45.7316 | 1.0429 | 2.391% | 2.22% | 4.61% | 7.1532 | 11.2504 | 5.2288 | -1.262% | 4.007% | -0.3547% | 24.64% | 2.499% | 51.07% | 4.61% | 45.6 | 40.83 | 4.77 | -1.229% | 4.619% | 3.39% | 5.38 | 11.11 | 2.22 | -1.208% | -0.2119% | 0.1483% | 3.8% | -1.46% | 31.33% | 3.37%
39 | 8-Zone Comissioned | 8-Zone Commissioned | Minneapolis | Zn Cooling Linear | 53.2778 | 35.8669 | 17.4109 | 1.2% | 5.103% | 6.303% | 6.5514 | 4.7266 | 2.4898 | -0.6165% | 1.76% | 0.05659% | 18.88% | 1.867% | 14.29% | 6.303% | 62.5537 | 32.9707 | 29.5831 | -1.024% | 1.883% | 0.8589% | 5.36 | 4.1949 | 1.2846 | -0.9764% | -0.1295% | 0.08218% | 5.007% | -1.998% | 3.86% | 0.8589%
40 | 8-Zone Comissioned | 8-Zone Commissioned | Seattle | Zn Cooling Linear | 34.4685 | 30.5813 | 3.8872 | 5.453% | 6.419% | 11.87% | 5.4047 | 1.6579 | 1.4195 | -1.596% | 3.758% | 3.29% | 14.99% | 6.519% | 39.24% | 11.87% | 37.53 | 28.36 | 9.17 | 1.189% | 7.763% | 8.952% | 4.33 | 1.27 | 0.64 | -2.28% | 2.208% | 1.237% | 9.3% | 1.69% | 25.85% | 8.94%
41 | 8-Zone Comissioned | 8-Zone Commissioned | New York | Zn Cooling T&R | 44.7186 | 36.6756 | 8.043 | 2.265% | 3.945% | 6.209% | 5.5029 | 5.9632 | 3.1103 | 0.1924% | 1.99% | 0.08225% | 7.367% | 2.86% | 18.95% | 6.209% | 47.77 | 34.14 | 13.63 | -1.284% | 3.953% | 2.669% | 5.69 | 4.95 | 1.37 | -2.547% | 0.978% | 0.2852% | 10.1% | -1.86% | 12.49% | 2.69%
42 | 8-Zone Comissioned | 8-Zone Commissioned | Houston | Zn Cooling T&R | 46.5629 | 45.298 | 1.265 | 3.275% | 1.767% | 5.042% | 6.4114 | 11.563 | 5.2243 | 0.2506% | 3.37% | -0.3455% | 11.98% | 3.424% | 40.65% | 5.042% | 45.83 | 40.94 | 4.89 | -1.462% | 4.364% | 2.903% | 6.36 | 10.24 | 2.21 | -3.284% | 1.631% | 0.1695% | 5.9% | -1.74% | 29.64% | 2.88%
43 | 8-Zone Comissioned | 8-Zone Commissioned | Minneapolis | Zn Cooling T&R | 53.3568 | 35.4701 | 17.8867 | 1.898% | 4.266% | 6.164% | 5.8743 | 4.9506 | 2.546 | 0.5742% | 1.366% | -0.04233% | 6.846% | 2.953% | 11.94% | 6.164% | 62.8955 | 33.1789 | 29.7166 | -1.354% | 1.671% | 0.3172% | 5.8697 | 3.91 | 1.2637 | -1.784% | 0.322% | 0.1153% | 7.2% | -2.64% | 3.43% | 0.32%
44 | 8-Zone Comissioned | 8-Zone Commissioned | Seattle | Zn Cooling T&R | 34.9732 | 30.3575 | 4.6157 | 6.025% | 4.556% | 10.58% | 4.368 | 2.0554 | 1.835 | 1.055% | 2.742% | 2.228% | 1.487% | 7.204% | 27.85% | 10.58% | 38.25 | 28.66 | 9.59 | 0.4609% | 6.744% | 7.205% | 4.14 | 1.56 | 0.82 | -1.82% | 1.504% | 0.8006% | 7.8% | 0.68% | 22.49% | 7.22%
45 | 8-Zone Comissioned | 8-Zone Commissioned | New York | Max Zn Damper Var Limits T&R | 46.0573 | 37.1834 | 8.8739 | 1.2% | 2.202% | 3.401% | 5.5861 | 6.6295 | 2.8686 | 0.01799% | 0.5925% | 0.5892% | 16.32% | 1.515% | 10.58% | 3.401% | 48.18 | 33.33 | 14.85 | 0.3667% | 1.467% | 1.834% | 4.54 | 5.24 | 1.42 | -0.2037% | 0.3871% | 0.1834% | 5.4% | 0.55% | 4.64% | 1.85%
46 | 8-Zone Comissioned | 8-Zone Commissioned | Houston | Max Zn Damper Var Limits T&R | 48.3075 | 46.3753 | 1.9322 | 1.078% | 0.4061% | 1.484% | 6.5386 | 12.9013 | 4.8363 | -0.008722% | 0.6405% | 0.4459% | 22.8% | 1.127% | 9.342% | 1.484% | 46.06 | 40.06 | 6 | 0.4025% | 2.013% | 2.415% | 4.93 | 10.82 | 2.19 | -0.2542% | 0.4025% | 0.2119% | 2% | 0.45% | 13.66% | 2.4%
47 | 8-Zone Comissioned | 8-Zone Commissioned | Minneapolis | Max Zn Damper Var Limits T&R | 54.9223 | 36.2512 | 18.6711 | 0.5241% | 2.887% | 3.411% | 6.1676 | 5.6209 | 2.3635 | 0.0584% | 0.1871% | 0.2786% | 19.25% | 0.8153% | 8.082% | 3.411% | 63.0242 | 32.2118 | 30.8124 | 0.1791% | -0.06575% | 0.1133% | 4.8147 | 3.99 | 1.28 | -0.1121% | 0.1952% | 0.08946% | 1.8% | 0.35% | -0.13% | 0.11%
48 | 8-Zone Comissioned | 8-Zone Commissioned | Seattle | Max Zn Damper Var Limits T&R | 36.2988 | 31.0479 | 5.2509 | 4.26% | 2.932% | 7.192% | 4.5692 | 2.4906 | 1.8889 | 0.5405% | 1.63% | 2.09% | 8.472% | 5.093% | 17.93% | 7.192% | 39.2 | 28.47 | 10.73 | 0.9219% | 3.979% | 4.901% | 3.64 | 1.77 | 0.93 | -0.6065% | 0.9947% | 0.5337% | 4.6% | 1.31% | 13.25% | 4.89%
49 | N/A | 15-Zone Commissioned | New York | ASHRAE Guideline 36 | 48.2024 | 37.7944 | 10.408 | 0.6893% | 2.117% | 2.806% | 5.5484 | 6.668 | 2.9187 | -0.7158% | 0.714% | 0.6911% | 11.41% | 0.8964% | 9.164% | 2.806%
50 | N/A | 25-Zone Commissioned | New York | ASHRAE Guideline 36 | 47.5418 | 35.7123 | 11.8295 | 0.8623% | 1.532% | 2.394% | 4.9884 | 6.2812 | 2.7862 | -0.04584% | 0.4585% | 0.4497% | 10.43% | 1.162% | 5.934% | 2.394%
51 | N/A | 15-Zone Commissioned | New York | Max Zn Damper T&R | 47.2442 | 37.021 | 10.2232 | 2.249% | 2.49% | 4.739% | 5.3913 | 5.8342 | 3.1362 | -0.3991% | 2.395% | 0.2527% | 7.562% | 2.925% | 10.78% | 4.739%
52 | N/A | 25-Zone Commissioned | New York | Max Zn Damper T&R | 46.5474 | 35.1747 | 11.3727 | 1.966% | 2.47% | 4.436% | 5.0008 | 5.56 | 2.9575 | -0.07116% | 1.939% | 0.09805% | 7.428% | 2.65% | 9.566% | 4.436%
53 | N/A | 15-Zone Commissioned | New York | Avg Zn Damper Linear | 44.974 | 37.0391 | 7.9349 | 2.212% | 7.104% | 9.316% | 5.8415 | 5.621 | 2.9173 | -1.307% | 2.825% | 0.694% | 10.47% | 2.877% | 30.75% | 9.316%
54 | N/A | 25-Zone Commissioned | New York | Avg Zn Damper Linear | 44.2555 | 35.0469 | 9.2085 | 2.228% | 6.913% | 9.141% | 5.5642 | 5.1907 | 2.6356 | -1.228% | 2.697% | 0.7589% | 17.94% | 3.004% | 26.78% | 9.141%
55 | N/A | 15-Zone Commissioned | New York | Zn Cooling − Zn Heating Linear | 45.293 | 37.0897 | 8.2033 | 2.11% | 6.563% | 8.673% | 5.4424 | 5.9362 | 3.0519 | -0.5022% | 2.19% | 0.4227% | 6.062% | 2.744% | 28.41% | 8.673%
56 | N/A | 25-Zone Commissioned | New York | Zn Cooling − Zn Heating Linear | 44.1902 | 34.8739 | 9.3164 | 2.584% | 6.692% | 9.275% | 5.0412 | 5.3973 | 2.7789 | -0.1542% | 2.273% | 0.4647% | 10.24% | 3.483% | 25.92% | 9.275%
57 | N/A | 15-Zone Commissioned | New York | Zn Cooling Linear | 44.9759 | 37.2857 | 7.6902 | 1.715% | 7.597% | 9.312% | 5.9331 | 5.6667 | 3.0266 | -1.492% | 2.733% | 0.4737% | 15.73% | 2.23% | 32.88% | 9.312%
58 | N/A | 25-Zone Commissioned | New York | Zn Cooling Linear | 44.2702 | 35.3081 | 8.9621 | 1.692% | 7.419% | 9.111% | 5.6865 | 5.2573 | 2.7079 | -1.479% | 2.561% | 0.6106% | 22.56% | 2.281% | 28.73% | 9.111%
59 | N/A | 15-Zone Commissioned | New York | Zn Heating Linear | 47.1457 | 37.8058 | 9.3399 | 0.6664% | 4.271% | 4.937% | 5.1117 | 6.8407 | 3.1941 | 0.1647% | 0.3658% | 0.1359% | 7.025% | 0.8666% | 18.49% | 4.937%
60 | N/A | 25-Zone Commissioned | New York | Zn Heating Linear | 45.797 | 35.5025 | 10.2945 | 1.293% | 4.684% | 5.977% | 4.9631 | 6.1003 | 2.7827 | 0.006224% | 0.8298% | 0.4569% | 11.44% | 1.743% | 18.14% | 5.977%
61 | N/A | 15-Zone Commissioned | New York | Zn Cooling − Zn Heating T&R | 45.7467 | 37.2825 | 8.4642 | 1.722% | 6.036% | 7.758% | 5.2666 | 6.1727 | 3.1839 | -0.1476% | 1.713% | 0.1564% | 6.302% | 2.239% | 26.13% | 7.758%
62 | N/A | 25-Zone Commissioned | New York | Zn Cooling − Zn Heating T&R | 44.7893 | 35.0623 | 9.727 | 2.197% | 5.849% | 8.045% | 4.9119 | 5.609 | 2.885 | 0.1113% | 1.838% | 0.2469% | 11.09% | 2.961% | 22.65% | 8.045%
63 | N/A | 15-Zone Commissioned | New York | Zn Cooling T&R | 45.1502 | 36.804 | 8.3462 | 2.686% | 6.275% | 8.961% | 5.0794 | 5.9055 | 3.1598 | 0.2299% | 2.251% | 0.205% | 3.806% | 3.493% | 27.16% | 8.961%
64 | N/A | 25-Zone Commissioned | New York | Zn Cooling T&R | 44.7684 | 34.9184 | 9.8499 | 2.492% | 5.596% | 8.088% | 4.9142 | 5.4756 | 2.8721 | 0.1065% | 2.112% | 0.2733% | 8.08% | 3.359% | 21.68% | 8.088%
67 | N/A | 15-Zone Commissioned | New York | OAT Linear | 46.1662 | 37.7096 | 8.4565 | 0.8602% | 6.052% | 6.912% | 5.5022 | 6.6471 | 2.901 | -0.6228% | 0.7561% | 0.7269% | 13.07% | 1.119% | 26.2% | 6.912%
68 | N/A | 25-Zone Commissioned | New York | OAT Linear | 45.2022 | 35.6642 | 9.538 | 0.961% | 6.237% | 7.198% | 5.1527 | 6.1771 | 2.6779 | -0.3832% | 0.6721% | 0.672% | 19.7% | 1.295% | 24.16% | 7.198%
69 | N/A | 15-Zone Commissioned | New York | RAT Linear | 46.0628 | 36.9434 | 9.1194 | 2.405% | 4.716% | 7.121% | 4.7248 | 6.4147 | 3.1447 | 0.9449% | 1.225% | 0.2356% | 5.386% | 3.128% | 20.41% | 7.121%
70 | N/A | 25-Zone Commissioned | New York | RAT Linear | 45.5265 | 35.4416 | 10.0849 | 1.418% | 5.114% | 6.532% | 5.081 | 5.9302 | 2.774 | -0.2358% | 1.179% | 0.4748% | 10.5% | 1.911% | 19.81% | 6.532%
71 | N/A | 15-Zone Commissioned | New York | Max Zn Damper Var Limits T&R | 47.8561 | 37.2896 | 10.5665 | 1.707% | 1.798% | 3.505% | 5.3899 | 6.4451 | 2.7953 | -0.3963% | 1.164% | 0.9399% | 10.67% | 2.22% | 7.781% | 3.505%
72 | N/A | 25-Zone Commissioned | New York | Max Zn Damper Var Limits T&R | 47.3384 | 35.4768 | 11.8615 | 1.346% | 1.466% | 2.812% | 4.9727 | 6.157 | 2.6907 | -0.01345% | 0.7133% | 0.6457% | 10.56% | 1.814% | 5.679% | 2.812%
73 | 8-Zone FaultsLow | 8-Zone FaultsLow | New York | ASHRAE Guideline 36 | 51.3516 | 39.6481 | 11.7035 | 0.6591% | 3.659% | 4.318% | 7.4028 | 7.2637 | 2.8823 | -0.1026% | 0.3474% | 0.4143% | 15.78% | 0.7514% | 13.86% | 4.078% | 49.34 | 35.13 | 14.21 | -1.055% | 6.371% | 5.316% | 6.62 | 5.13 | 1.25 | -2.725% | 1.151% | 0.5181% | 9.8% | -1.57% | 18.94% | 5.33%
74 | 8-Zone FaultsModerate | N/A | New York | ASHRAE Guideline 36 | [16 empty] | 48.91 | 34.71 | 14.2 | -0.3262% | 11.69% | 11.36% | 6.47 | 4.88 | 1.24 | -3.335% | 2.32% | 0.6705% | 9.8% | -0.52% | 31.26% | 11.38%
75 | N/A | 15-Zone FaultsLow | New York | ASHRAE Guideline 36 | 51.3597 | 38.8464 | 12.5134 | 0.8088% | 1.912% | 2.721% | 6.2466 | 7.0052 | 2.9352 | -0.4529% | 0.6458% | 0.6159% | 10.52% | 0.9457% | 6.597% | 2.385%
76 | N/A | 25-Zone FaultsLow | New York | ASHRAE Guideline 36 | 49.6069 | 36.0546 | 13.5523 | 0.2721% | 0.3187% | 0.5908% | 5.5185 | 6.2434 | 2.6363 | -0.03578% | 0.1073% | 0.2005% | 12.26% | 0.09887% | 0.2411% | 0.1378%
77 | 8-Zone FaultsLow | 8-Zone FaultsLow | New York | Max Zn Damper T&R | 58.8882 | 41.328 | 17.5603 | -2.471% | -7.254% | -9.725% | 8.5448 | 7.5628 | 3.1212 | -2.23% | -0.2098% | -0.03069% | 29.59% | -3.454% | -29.25% | -10% | 52.66 | 34.65 | 18.01 | -0.1343% | -0.9211% | -1.055% | 5.68 | 5.32 | 1.52 | -0.9211% | 0.7868% | 0% | 7.9% | -0.2% | -2.78% | -1.07%
78 | 8-Zone FaultsModerate | N/A | New York | Max Zn Damper T&R | [16 empty] | 55.58 | 34.28 | 21.3 | 0.4531% | -1.178% | -0.7249% | 4.87 | 5.67 | 1.61 | -0.4349% | 0.888% | 0% | 9.2% | 0.73% | -3.13% | -0.71%
79 | N/A | 15-Zone FaultsLow | New York | Max Zn Damper T&R | 57.6003 | 39.9024 | 17.6979 | -1.191% | -7.908% | -9.099% | 6.6049 | 7.3587 | 3.2794 | -1.132% | -0.02376% | -0.03599% | 15.38% | -1.747% | -32.1% | -9.476%
80 | N/A | 25-Zone FaultsLow | New York | Max Zn Damper T&R | 53.842 | 36.4923 | 17.3498 | -0.605% | -7.291% | -7.896% | 5.8004 | 6.3039 | 2.7315 | -0.6008% | -0.01398% | 0.00982% | 18.99% | -1.114% | -27.71% | -8.388%
81 | 8-Zone FaultsLow | 8-Zone FaultsLow | New York | Avg Zn Damper Linear | 49.6804 | 38.8749 | 10.8055 | 2.1% | 5.332% | 7.432% | 7.2102 | 6.5044 | 3.0611 | 0.2564% | 1.762% | 0.08118% | 6.852% | 2.687% | 20.47% | 7.199% | 50.32 | 35.09 | 15.23 | -0.9787% | 4.414% | 3.435% | 6.55 | 5.06 | 1.35 | -2.591% | 1.286% | 0.3262% | 8.4% | -1.46% | 13.1% | 3.44%
82 | 8-Zone FaultsModerate | N/A | New York | Avg Zn Damper Linear | [16 empty] | 51.13 | 34.25 | 16.88 | 0.5074% | 6.832% | 7.34% | 5.57 | 5.12 | 1.43 | -1.704% | 1.885% | 0.3262% | 8% | 0.83% | 18.29% | 7.36%
83 | N/A | 15-Zone FaultsLow | New York | Avg Zn Damper Linear | 47.669 | 38.1328 | 9.5363 | 2.16% | 7.551% | 9.712% | 6.4895 | 5.9934 | 2.9906 | -0.9128% | 2.562% | 0.511% | 6.991% | 2.765% | 28.82% | 9.399%
84 | N/A | 25-Zone FaultsLow | New York | Avg Zn Damper Linear | 46.0419 | 35.715 | 10.327 | 0.9527% | 6.782% | 7.735% | 6.0622 | 5.4025 | 2.5938 | -1.125% | 1.792% | 0.2857% | 14.34% | 1.04% | 23.98% | 7.314%
85 | 8-Zone FaultsLow | 8-Zone FaultsLow | New York | Zn Cooling − Zn Heating Linear | 48.8939 | 39.183 | 9.7109 | 1.526% | 7.372% | 8.897% | 7.5378 | 6.4285 | 3.1175 | -0.3541% | 1.904% | -0.02388% | 12.75% | 1.916% | 28.52% | 8.669% | 49.95 | 35.25 | 14.7 | -1.286% | 5.431% | 4.145% | 6.1 | 5.65 | 1.38 | -1.727% | 0.1535% | 0.2687% | 8.2% | -1.94% | 16.1% | 4.13%
86 | 8-Zone FaultsModerate | N/A | New York | Zn Cooling − Zn Heating Linear | [16 empty] | 50.48 | 34.66 | 15.82 | -0.2356% | 8.753% | 8.518% | 5.4 | 5.71 | 1.41 | -1.395% | 0.8155% | 0.3625% | 6.7% | -0.35% | 23.42% | 8.54%
87 | N/A | 15-Zone FaultsLow | New York | Zn Cooling − Zn Heating Linear | 47.2252 | 38.022 | 9.2032 | 2.37% | 8.182% | 10.55% | 6.2041 | 6.1189 | 3.0397 | -0.3723% | 2.325% | 0.4179% | 5.617% | 3.048% | 31.3% | 10.24%
88 | N/A | 25-Zone FaultsLow | New York | Zn Cooling − Zn Heating Linear | 45.6065 | 35.7106 | 9.8959 | 0.9613% | 7.646% | 8.607% | 5.9099 | 5.5106 | 2.6337 | -0.8201% | 1.576% | 0.2057% | 12.29% | 1.052% | 27.16% | 8.191%
89 | 8-Zone FaultsLow | 8-Zone FaultsLow | New York | Zn Cooling Linear | 48.1906 | 39.4483 | 8.7423 | 1.031% | 9.176% | 10.21% | 8.2569 | 6.1075 | 2.9847 | -1.694% | 2.502% | 0.2235% | 22.37% | 1.252% | 35.65% | 9.982% | 49.97 | 35.36 | 14.61 | -1.497% | 5.604% | 4.107% | 6.34 | 5.51 | 1.37 | -2.188% | 0.4222% | 0.2879% | 9.3% | -2.25% | 16.64% | 4.1%
90 | 8-Zone FaultsModerate | N/A | New York | Zn Cooling Linear | [16 empty] | 50.23 | 34.54 | 15.69 | -0.01812% | 8.989% | 8.971% | 5.53 | 5.49 | 1.38 | -1.631% | 1.214% | 0.4168% | 7.4% | 0% | 24.02% | 8.99%
91 | N/A | 15-Zone FaultsLow | New York | Zn Cooling Linear | 47.0462 | 38.4706 | 8.5756 | 1.521% | 9.371% | 10.89% | 6.8684 | 5.9469 | 2.996 | -1.631% | 2.65% | 0.5008% | 16.48% | 1.904% | 35.99% | 10.58%
92 | N/A | 25-Zone FaultsLow | New York | Zn Cooling Linear | 45.5582 | 36.1455 | 9.4127 | 0.09002% | 8.614% | 8.704% | 6.4608 | 5.4007 | 2.6276 | -1.924% | 1.796% | 0.218% | 22.93% | -0.1529% | 30.71% | 8.288%
93 | 8-Zone FaultsLow | 8-Zone FaultsLow | New York | Zn Heating Linear | 51.6893 | 39.4212 | 12.2681 | 1.082% | 2.607% | 3.689% | 7.223 | 7.0565 | 3.0425 | 0.2324% | 0.7335% | 0.1159% | 15.76% | 1.319% | 9.702% | 3.447% | 49.68 | 35.7 | 13.98 | -2.149% | 6.813% | 4.663% | 7.06 | 5.26 | 1.25 | -3.569% | 0.9019% | 0.5181% | 10.9% | -3.22% | 20.26% | 4.68%
94 | 8-Zone FaultsModerate | N/A | New York | Zn Heating Linear | [16 empty] | 49.84 | 34.38 | 15.46 | 0.2718% | 9.406% | 9.677% | 5.74 | 5.25 | 1.27 | -2.012% | 1.649% | 0.6162% | 7.9% | 0.44% | 25.15% | 9.69%
95 | N/A | 15-Zone FaultsLow | New York | Zn Heating Linear | 49.4555 | 38.4992 | 10.9563 | 1.466% | 4.862% | 6.328% | 5.7093 | 7.0037 | 3.127 | 0.5648% | 0.6487% | 0.2527% | 6.228% | 1.831% | 18.22% | 6.004%
96 | N/A | 25-Zone FaultsLow | New York | Zn Heating Linear | 46.448 | 35.4387 | 11.0093 | 1.506% | 5.415% | 6.921% | 5.4225 | 5.8611 | 2.4986 | 0.1565% | 0.8734% | 0.4764% | 11.04% | 1.805% | 18.96% | 6.497%
97 | 8-Zone FaultsLow | 8-Zone FaultsLow | New York | Zn Cooling − Zn Heating T&R | 49.4619 | 39.1004 | 10.3615 | 1.68% | 6.159% | 7.839% | 7.229 | 6.6166 | 3.1557 | 0.2214% | 1.553% | -0.09499% | 10.46% | 2.123% | 23.74% | 7.608% | 49.87 | 35.04 | 14.83 | -0.8827% | 5.181% | 4.299% | 6.21 | 5.36 | 1.34 | -1.938% | 0.71% | 0.3454% | 8.8% | -1.31% | 15.38% | 4.3%
98 | 8-Zone FaultsModerate | N/A | New York | Zn Cooling − Zn Heating T&R | [16 empty] | 50.67 | 34.71 | 15.96 | -0.3262% | 8.499% | 8.173% | 5.73 | 5.47 | 1.39 | -1.993% | 1.25% | 0.3987% | 8.2% | -0.51% | 22.73% | 8.19%
99 | N/A | 15-Zone FaultsLow | New York | Zn Cooling − Zn Heating T&R | 48.3476 | 38.4705 | 9.8772 | 1.521% | 6.906% | 8.426% | 6.1757 | 6.4699 | 3.1656 | -0.3185% | 1.66% | 0.1796% | 6.228% | 1.904% | 26.27% | 8.109%
100 | N/A | 25-Zone FaultsLow | New York | Zn Cooling − Zn Heating T&R | 46.0226 | 35.6978 | 10.3247 | 0.987% | 6.787% | 7.774% | 5.6511 | 5.6762 | 2.7141 | -0.3015% | 1.244% | 0.04465% | 12.5% | 1.087% | 24% | 7.353%
101 | 8-Zone FaultsLow | 8-Zone FaultsLow | New York | Zn Cooling T&R | 49.1898 | 39.0726 | 10.1172 | 1.731% | 6.615% | 8.346% | 7.3251 | 6.4906 | 3.1577 | 0.04233% | 1.788% | -0.09884% | 8.987% | 2.192% | 25.53% | 8.116% | 50.28 | 34.7 | 15.58 | -0.2303% | 3.742% | 3.512% | 5.85 | 5.38 | 1.35 | -1.247% | 0.6717% | 0.3262% | 8.1% | -0.34% | 11.12% | 3.52%
102 | 8-Zone FaultsModerate | N/A | New York | Zn Cooling T&R | [16 empty] | 52.07 | 34.32 | 17.75 | 0.3806% | 5.256% | 5.636% | 5.28 | 5.46 | 1.46 | -1.178% | 1.269% | 0.2718% | 7.6% | 0.61% | 14.04% | 5.64%
103 | N/A | 15-Zone FaultsLow | New York | Zn Cooling T&R | 47.6735 | 37.9508 | 9.7227 | 2.505% | 7.198% | 9.703% | 5.9405 | 6.2302 | 3.1209 | 0.127% | 2.114% | 0.2642% | 3.83% | 3.229% | 27.43% | 9.391%
104 | N/A | 25-Zone FaultsLow | New York | Zn Cooling T&R | 46.1899 | 35.5998 | 10.5901 | 1.183% | 6.255% | 7.438% | 5.5898 | 5.6173 | 2.7362 | -0.1788% | 1.362% | 0.0002513% | 9.013% | 1.359% | 22.05% | 7.016%
105 | 8-Zone FaultsLow | 8-Zone FaultsLow | New York | Max Zn Damper Var Limits T&R | 57.5241 | 40.6791 | 16.8449 | -1.262% | -5.921% | -7.183% | 7.9662 | 7.5285 | 3.0853 | -1.152% | -0.1459% | 0.03607% | 28.22% | -1.829% | -23.99% | -7.452% | 52.79 | 34.4 | 18.39 | 0.3454% | -1.65% | -1.305% | 5.1 | 5.66 | 1.5 | 0.1919% | 0.1343% | 0.03838% | 6.6% | 0.53% | -4.93% | -1.3%
106 | 8-Zone FaultsModerate | N/A | New York | Max Zn Damper Var Limits T&R | [16 empty] | 56.12 | 34.38 | 21.74 | 0.2718% | -1.975% | -1.704% | 4.61 | 6.06 | 1.58 | 0.03625% | 0.1812% | 0.05437% | 8.7% | 0.44% | -5.26% | -1.7%
107 | N/A | 15-Zone FaultsLow | New York | Max Zn Damper Var Limits T&R | 56.5392 | 39.6174 | 16.9218 | -0.6516% | -6.437% | -7.089% | 6.4025 | 7.3225 | 3.2331 | -0.7482% | 0.04481% | 0.05174% | 14.1% | -1.02% | -26.31% | -7.46%
108 | N/A | 25-Zone FaultsLow | New York | Max Zn Damper Var Limits T&R | 53.0538 | 36.3679 | 16.6859 | -0.3558% | -5.961% | -6.317% | 5.7155 | 6.2825 | 2.7136 | -0.4305% | 0.02899% | 0.04569% | 18.16% | -0.7693% | -22.83% | -6.801%

## Baseline Figures
Baseline | Figure 3
|  |  | Fan Electricity | Cooling Electricity | Pump Electricity | Total Electricity | Total Gas | Lighting/Equipment | Total
New York | 8-Zone Comm.
|  | E+ | 5.5946 | 6.912 | 3.1495 | 37.7554 | 9.9238 | 22.0992 | 47.6791
|  | BRS | 4.44 | 5.43 | 1.51 | 33.51 | 15.57 | 22.13 | 49.08
15-Zone Comm.
|  | E+ | 5.1934 | 7.0221 | 3.2615 | 38.1363 | 11.458 | 22.6593 | 49.5943
25-Zone Comm.
|  | E+ | 4.9661 | 6.5045 | 3.0052 | 36.1323 | 12.5757 | 21.6564 | 48.708
8-Zone Faults Low
|  | E+ | 7.3478 | 7.4502 | 3.1047 | 40.0018 | 13.6672 | 22.0992 | 53.6691
|  | BRS | 5.2 | 5.73 | 1.52 | 34.58 | 17.53 | 22.13 | 52.11
8-Zone Faults Mod.
|  | BRS | 4.63 | 6.16 | 1.61 | 34.53 | 20.65 | 22.13 | 55.18
15-Zone Faults Low
|  | E+ | 6.0075 | 7.3462 | 3.2604 | 39.2734 | 13.523 | 22.6593 | 52.7964
25-Zone Faults Low
|  | E+ | 5.5006 | 6.2969 | 2.7364 | 36.1904 | 13.7113 | 21.6564 | 49.9017
Houston | 8-Zone Comm.
|  | E+ | 6.5343 | 13.2154 | 5.0549 | 46.9038 | 2.1313 | 22.0992 | 49.035
|  | BRS | 4.81 | 11.01 | 2.29 | 40.25 | 6.95 | 22.14 | 47.2
Minneapolis | 8-Zone Comm.
|  | E+ | 6.2008 | 5.7273 | 2.5219 | 36.5493 | 20.3127 | 22.0992 | 56.8619
|  | BRS | 4.744 | 4.1132 | 1.3364 | 32.3248 | 30.7709 | 22.1311 | 63.0957
Seattle | 8-Zone Comm.
|  | E+ | 4.7806 | 3.128 | 2.7063 | 32.7141 | 6.3978 | 22.0992 | 39.1119
|  | BRS | 3.39 | 2.18 | 1.15 | 28.85 | 12.37 | 22.13 | 41.22

## Savings Figures
Figure 4 | EnergyPlus and BRS modeled SAT reset savings for New York
|  |  | Electricity Savings | Natural Gas Savings | Total Savings |  | Figure 10 | SAT reset strategies savings vs. number of zones; modeled in EnergyPlus for New York
[10 empty] | Electricity Savings | Natural Gas Savings | Total | Unmet Thermostat
New York | ASHRAE Guideline 36 | [5 empty] | New York | ASHRAE Guideline 36
|  | E+ | 0.9946% | 4.188% | 5.182% |  |  |  | 8-Zone | 0.9946% | 4.188% | 5.182% | 15.13%
|  | BRS | -0.978% | 5.522% | 4.544% |  |  |  | 15-Zone | 0.6893% | 2.117% | 2.806% | 11.41%
[9 empty] | 25-Zone | 0.8623% | 1.532% | 2.394% | 10.43%
Avg Zn Damper Linear
|  | E+ | 2.448% | 4.185% | 6.633% |  |  | Avg Zn Damper Linear
|  | BRS | -2.18% | 4.177% | 1.997% |  |  |  | 8-Zone | 2.448% | 4.185% | 6.633% | 7.228%
[9 empty] | 15-Zone | 2.212% | 7.104% | 9.316% | 10.47%
| Max Zn Damper Var Limits T&R | [7 empty] | 25-Zone | 2.228% | 6.913% | 9.141% | 17.94%
|  | E+ | 1.2% | 2.202% | 3.401%
|  | BRS | 0.3667% | 1.467% | 1.834% |  |  | Max Zn Damper Var Limits T&R
[9 empty] | 8-Zone | 1.2% | 2.202% | 3.401% | 16.32%
| Max Zn Damper T&R | [7 empty] | 15-Zone | 1.707% | 1.798% | 3.505% | 10.67%
|  | E+ | 2.393% | 2.461% | 4.854% |  |  |  | 25-Zone | 1.346% | 1.466% | 2.812% | 10.56%
|  | BRS | -0.3464% | 1.854% | 1.508%
Max Zn Damper T&R
| OAT Linear | [7 empty] | 8-Zone | 2.393% | 2.461% | 4.854% | 10.12%
|  | E+ | 0.4213% | 5.006% | 5.428% |  |  |  | 15-Zone | 1.807% | 1.149% | 2.955% | 8.867%
|  | BRS | -0.2241% | 4.544% | 4.319% |  |  |  | 25-Zone | 1.52% | 1.096% | 2.616% | 9.48%
| RAT "Bad Reset" Linear | [6 empty] | OAT Linear
|  | E+ | 0.3023% | 5.454% | 5.756% |  |  |  | 8-Zone | 0.4213% | 5.006% | 5.428% | 20.27%
|  | BRS | -5.97% | 6.255% | 0.2852% |  |  |  | 15-Zone | 0.8602% | 6.052% | 6.912% | 13.07%
[9 empty] | 25-Zone | 0.961% | 6.237% | 7.198% | 19.7%
RAT Linear
|  | E+ | 0.733% | 3.252% | 3.985% |  |  | RAT "Bad Reset" Linear
|  | BRS | -0.1426% | 3.219% | 3.077% |  |  |  | 8-Zone | 0.3023% | 5.454% | 5.756% | 26.79%
| Zn Cooling − Zn Heating Linear | [6 empty] | RAT Linear
|  | E+ | 2.027% | 4.437% | 6.464% |  |  |  | 8-Zone | 0.733% | 3.252% | 3.985% | 13.8%
|  | BRS | -0.6927% | 4.584% | 3.892% |  |  |  | 15-Zone | 2.405% | 4.716% | 7.121% | 5.386%
[9 empty] | 25-Zone | 1.418% | 5.114% | 6.532% | 10.5%
Zn Cooling − Zn Heating T&R
|  | E+ | 1.732% | 3.855% | 5.587% |  |  | Zn Cooling − Zn Heating Linear
|  | BRS | -1.61% | 5.155% | 3.545% |  |  |  | 8-Zone | 2.027% | 4.437% | 6.464% | 10.73%
[9 empty] | 15-Zone | 2.11% | 6.563% | 8.673% | 6.062%
| Zn Cooling Linear | [7 empty] | 25-Zone | 2.584% | 6.692% | 9.275% | 10.24%
|  | E+ | 1.562% | 5.17% | 6.732%
|  | BRS | -0.9372% | 4.34% | 3.403% |  |  | Zn Cooling − Zn Heating T&R
[9 empty] | 8-Zone | 1.732% | 3.855% | 5.587% | 10.13%
| Zn Cooling T&R | [7 empty] | 15-Zone | 1.722% | 6.036% | 7.758% | 6.302%
|  | E+ | 2.265% | 3.945% | 6.209% |  |  |  | 25-Zone | 2.197% | 5.849% | 8.045% | 11.09%
|  | BRS | -1.284% | 3.953% | 2.669%
Zn Cooling Linear
| Zn Heating Linear | [7 empty] | 8-Zone | 1.562% | 5.17% | 6.732% | 20.26%
|  | E+ | 0.8768% | 1.034% | 1.911% |  |  |  | 15-Zone | 1.715% | 7.597% | 9.312% | 15.73%
|  | BRS | -0.8354% | 5.073% | 4.238% |  |  |  | 25-Zone | 1.692% | 7.419% | 9.111% | 22.56%
Zn Cooling T&R
[9 empty] | 8-Zone | 2.265% | 3.945% | 6.209% | 7.367%
[9 empty] | 15-Zone | 2.582% | 5.927% | 8.509% | 4.201%
[9 empty] | 25-Zone | 2.44% | 5.175% | 7.615% | 9.009%
Figure 11 | SAT reset strategies savings vs. fault level; modeled in the BRS for New York | [6 empty] | Zn Heating Linear
New York |  | Electricity Savings | Natural Gas Savings | Total | Unmet Thermostat |  |  |  | 8-Zone | 0.8768% | 1.034% | 1.911% | 13%
ASHRAE Guideline 36 | [8 empty] | 15-Zone | 0.6664% | 4.271% | 4.937% | 7.025%
| Commissioned | -0.978% | 5.522% | 4.544% | 10.1% |  |  |  | 25-Zone | 1.293% | 4.684% | 5.977% | 11.44%
| Faults Low | -1.055% | 6.371% | 5.316% | 9.8%
| Faults Moderate | -0.3262% | 11.69% | 11.36% | 9.8%
Avg Zn Damper Linear
| Commissioned | -2.18% | 4.177% | 1.997% | 10.2%
| Faults Low | -0.9787% | 4.414% | 3.435% | 8.4%
| Faults Moderate | 0.5074% | 6.832% | 7.34% | 8%
Max Zn Damper Var Limits T&R
| Commissioned | 0.3667% | 1.467% | 1.834% | 5.4%
| Faults Low | 0.3454% | -1.65% | -1.305% | 6.6%
| Faults Moderate | 0.2718% | -1.975% | -1.704% | 8.7%
Max Zn Damper T&R
| Commissioned | -0.3464% | 1.854% | 1.508% | 6.5%
| Faults Low | -0.1343% | -0.9211% | -1.055% | 7.9%
| Faults Moderate | 0.4531% | -1.178% | -0.7249% | 9.2%
Zn Cooling − Zn Heating Linear
| Commissioned | -0.6927% | 4.584% | 3.892% | 7.6%
| Faults Low | -1.286% | 5.431% | 4.145% | 8.2%
| Faults Moderate | -0.2356% | 8.753% | 8.518% | 6.7%
Zn Cooling − Zn Heating T&R
| Commissioned | -1.61% | 5.155% | 3.545% | 10.5%
| Faults Low | -0.8827% | 5.181% | 4.299% | 8.8%
| Faults Moderate | -0.3262% | 8.499% | 8.173% | 8.2%
Zn Cooling Linear
| Commissioned | -0.9372% | 4.34% | 3.403% | 8%
| Faults Low | -1.497% | 5.604% | 4.107% | 9.3%
| Faults Moderate | -0.01812% | 8.989% | 8.971% | 7.4%
Zn Cooling T&R
| Commissioned | -1.284% | 3.953% | 2.669% | 10.1%
| Faults Low | -0.2303% | 3.742% | 3.512% | 8.1%
| Faults Moderate | 0.3806% | 5.256% | 5.636% | 7.6%
Zn Heating Linear
| Commissioned | -0.8354% | 5.073% | 4.238% | 9.3%
| Faults Low | -2.149% | 6.813% | 4.663% | 10.9%
| Faults Moderate | 0.2718% | 9.406% | 9.677% | 7.9%
Figure 12 | SAT reset strategies savings vs. fault level; modeled in EnergyPlus for New York
New York |  | Electricity Savings | Natural Gas Savings | Total
ASHRAE Guideline 36
| Commissioned | 0.9946% | 4.188% | 5.182%
| Faults Low | 0.6591% | 3.659% | 4.318%
Avg Zn Damper Linear
| Commissioned | 2.448% | 4.185% | 6.633%
| Faults Low | 2.1% | 5.332% | 7.432%
Max Zn Damper Var Limits T&R
| Commissioned | 1.2% | 2.202% | 3.401%
| Faults Low | -1.262% | -5.921% | -7.183%
Max Zn Damper T&R
| Commissioned | 2.393% | 2.461% | 4.854%
| Faults Low | -2.471% | -7.254% | -9.725%
Zn Cooling − Zn Heating Linear
| Commissioned | 2.027% | 4.437% | 6.464%
| Faults Low | 1.526% | 7.372% | 8.897%
Zn Cooling − Zn Heating T&R
| Commissioned | 1.732% | 3.855% | 5.587%
| Faults Low | 1.68% | 6.159% | 7.839%
Zn Cooling Linear
| Commissioned | 1.562% | 5.17% | 6.732%
| Faults Low | 1.031% | 9.176% | 10.21%
Zn Cooling T&R
| Commissioned | 2.265% | 3.945% | 6.209%
| Faults Low | 1.731% | 6.615% | 8.346%
Zn Heating Linear
| Commissioned | 0.8768% | 1.034% | 1.911%
| Faults Low | 1.082% | 2.607% | 3.689%
Figure 5 | Unmet thermostat percentage by reset strategy and climate for BRS and EnergyPlus 8-zone commissioned
Figure 6 | BRS modeled SAT reset savings and unmet thermostat percentages by climate 8-zone commissioned
|  | Electricity Savings | Natural Gas Savings | Total | EnergyPlus Unmet Thermostat % | BRS Unmet Thermostat %
ASHRAE Guideline 36
| New York | -0.978% | 5.522% | 4.544% | 15.13% | 10.1%
| Houston | 0.2119% | 4.979% | 5.191% | 20.97% | 3.7%
| Minneapolis | -1.317% | 2.458% | 1.141% | 13.92% | 7.73%
| Seattle | -0.8248% | 9.777% | 8.952% | 9.265% | 12%
Avg Zn Damper Linear
| New York | -2.18% | 4.177% | 1.997% | 7.228% | 10.2%
| Houston | -4.237% | 4.703% | 0.4661% | 11.23% | 7.5%
| Minneapolis | -2.019% | 1.949% | -0.06961% | 7.008% | 5.885%
| Seattle | 0.1213% | 7.351% | 7.472% | 5.677% | 10.7%
Max Zn Damper Var Limits T&R
| New York | 0.3667% | 1.467% | 1.834% | 16.32% | 5.4%
| Houston | 0.4025% | 2.013% | 2.415% | 22.8% | 2%
| Minneapolis | 0.1791% | -0.06575% | 0.1133% | 19.25% | 1.8%
| Seattle | 0.9219% | 3.979% | 4.901% | 8.472% | 4.6%
Max Zn Damper T&R
| New York | -0.3464% | 1.854% | 1.508% | 10.12% | 6.5%
| Houston | -0.5932% | 3.114% | 2.521% | 8.681% | 4%
| Minneapolis | -0.4959% | 0.1136% | -0.3823% | 14.18% | 2.686%
| Seattle | 0.7521% | 4.246% | 4.998% | 7.384% | 5.7%
OAT Linear
| New York | -0.2241% | 4.544% | 4.319% | 20.27% | 7.5%
| Houston | 1.208% | 3.369% | 4.576% | 23.24% | 2.5%
| Minneapolis | -1.1% | 2.405% | 1.305% | 23.46% | 6.451%
| Seattle | 0.3882% | 8.006% | 8.394% | 17.08% | 7.7%
RAT "Bad Reset" Linear
| New York | -5.97% | 6.255% | 0.2852% | 26.79% | 20.4%
| Houston | -10.13% | 6.25% | -3.877% | 34.37% | 21.1%
| Minneapolis | -4.994% | 3.066% | -1.929% | 24.74% | 16.68%
| Seattle | -3.154% | 10.55% | 7.399% | 22.52% | 17.9%
RAT Linear
| New York | -0.1426% | 3.219% | 3.077% | 13.8% | 6.1%
| Houston | -0.2331% | 3.326% | 3.093% | 22.44% | 3.1%
| Minneapolis | -0.2932% | 1.16% | 0.8665% | 12.38% | 2.942%
| Seattle | 0.8006% | 6.162% | 6.963% | 7.037% | 5.5%
Zn Cooling − Zn Heating Linear
| New York | -0.6927% | 4.584% | 3.892% | 10.73% | 7.6%
| Houston | -0.1483% | 4.725% | 4.576% | 15.95% | 3.2%
| Minneapolis | -0.6882% | 1.926% | 1.238% | 10.87% | 5.007%
| Seattle | 0.9219% | 8.176% | 9.098% | 3.374% | 7.7%
Zn Cooling − Zn Heating T&R
| New York | -1.61% | 5.155% | 3.545% | 10.13% | 10.5%
| Houston | -1.059% | 5.127% | 4.068% | 15.19% | 5.8%
| Minneapolis | -1.691% | 2.249% | 0.5582% | 8.738% | 8.2%
| Seattle | -0.04852% | 8.855% | 8.806% | 2.905% | 8.6%
Zn Cooling Linear
| New York | -0.9372% | 4.34% | 3.403% | 20.26% | 8%
| Houston | -1.229% | 4.619% | 3.39% | 24.64% | 3.8%
| Minneapolis | -1.024% | 1.883% | 0.8589% | 18.88% | 5.007%
| Seattle | 1.189% | 7.763% | 8.952% | 14.99% | 9.3%
Zn Cooling T&R
| New York | -1.284% | 3.953% | 2.669% | 7.367% | 10.1%
| Houston | -1.462% | 4.364% | 2.903% | 11.98% | 5.9%
| Minneapolis | -1.354% | 1.671% | 0.3172% | 6.846% | 7.2%
| Seattle | 0.4609% | 6.744% | 7.205% | 1.487% | 7.8%
Zn Heating Linear
| New York | -0.8354% | 5.073% | 4.238% | 13% | 9.3%
| Houston | -0.2542% | 5.148% | 4.894% | 25.64% | 4.7%
| Minneapolis | -1.334% | 2.067% | 0.7333% | 11.86% | 7.2%
| Seattle | 0.1941% | 9.267% | 9.461% | 8.403% | 9.3%
Figure 7 | EnergyPlus modeled SAT reset savings by climate 8-zone commissioned
|  | Electricity Savings | Natural Gas Savings | Total | Unmet Thermostat
ASHRAE Guideline 36
| New York | 0.9946% | 4.188% | 5.182% | 15.13%
| Houston | 1.119% | 1.053% | 2.173% | 20.97%
| Minneapolis | 0.7725% | 4.393% | 5.165% | 13.92%
| Seattle | 3.91% | 5.107% | 9.017% | 9.265%
Avg Zn Damper Linear
| New York | 2.448% | 4.185% | 6.633% | 7.228%
| Houston | 3.592% | 1.897% | 5.488% | 11.23%
| Minneapolis | 2.072% | 4.248% | 6.319% | 7.008%
| Seattle | 5.626% | 5.347% | 10.97% | 5.677%
Max Zn Damper Var Limits T&R
| New York | 1.2% | 2.202% | 3.401% | 16.32%
| Houston | 1.078% | 0.4061% | 1.484% | 22.8%
| Minneapolis | 0.5241% | 2.887% | 3.411% | 19.25%
| Seattle | 4.26% | 2.932% | 7.192% | 8.472%
Max Zn Damper T&R
| New York | 2.393% | 2.461% | 4.854% | 10.12%
| Houston | 3.806% | 1.61% | 5.416% | 8.681%
| Minneapolis | 1.692% | 3.022% | 4.713% | 14.18%
| Seattle | 4.483% | 2.684% | 7.167% | 7.384%
OAT Linear
| New York | 0.4213% | 5.006% | 5.428% | 20.27%
| Houston | 0.1209% | 1.101% | 1.222% | 23.24%
| Minneapolis | 0.8543% | 5.231% | 6.085% | 23.46%
| Seattle | 4.324% | 6.355% | 10.68% | 17.08%
RAT "Bad Reset" Linear
| New York | 0.3023% | 5.454% | 5.756% | 26.79%
| Houston | 0.6587% | 2.348% | 3.007% | 34.37%
| Minneapolis | 0.1068% | 5.366% | 5.472% | 24.74%
| Seattle | 4.592% | 6.86% | 11.45% | 22.52%
RAT Linear
| New York | 0.733% | 3.252% | 3.985% | 13.8%
| Houston | 1.619% | 1.167% | 2.786% | 22.44%
| Minneapolis | 1.071% | 3.874% | 4.945% | 12.38%
| Seattle | 4.536% | 3.443% | 7.978% | 7.037%
Zn Cooling − Zn Heating Linear
| New York | 2.027% | 4.437% | 6.464% | 10.73%
| Houston | 3.325% | 1.966% | 5.291% | 15.95%
| Minneapolis | 1.628% | 4.767% | 6.395% | 10.87%
| Seattle | 6.388% | 5.228% | 11.62% | 3.374%
Zn Cooling − Zn Heating T&R
| New York | 1.732% | 3.855% | 5.587% | 10.13%
| Houston | 2.941% | 1.719% | 4.66% | 15.19%
| Minneapolis | 1.94% | 4.064% | 6.005% | 8.738%
| Seattle | 5.311% | 4.394% | 9.705% | 2.905%
Zn Cooling Linear
| New York | 1.562% | 5.17% | 6.732% | 20.26%
| Houston | 2.391% | 2.22% | 4.61% | 24.64%
| Minneapolis | 1.2% | 5.103% | 6.303% | 18.88%
| Seattle | 5.453% | 6.419% | 11.87% | 14.99%
Zn Cooling T&R
| New York | 2.265% | 3.945% | 6.209% | 7.367%
| Houston | 3.275% | 1.767% | 5.042% | 11.98%
| Minneapolis | 1.898% | 4.266% | 6.164% | 6.846%
| Seattle | 6.025% | 4.556% | 10.58% | 1.487%
Zn Heating Linear
| New York | 0.8768% | 1.034% | 1.911% | 13%
| Houston | 1.938% | 0.9752% | 2.913% | 25.64%
| Minneapolis | 1.27% | 0.9743% | 2.244% | 11.86%
| Seattle | 2.967% | 1.965% | 4.932% | 8.403%

## Electricity Breakdown Figures
Figure 8 | BRS modeled SAT reset electricity savings breakdown by climate 8-zone commissioned
|  | Fan Savings | Cooling Savings | Pump Savings | Electricity Savings
ASHRAE Guideline 36
| New York | -2.689% | 1.161% | 0.5501% | -0.978%
| Houston | -1.314% | 1.081% | 0.4449% | 0.2119%
| Minneapolis | -2.083% | 0.5215% | 0.2445% | -1.317%
| Seattle | -4.779% | 2.596% | 1.383% | -0.8248%
Avg Zn Damper Linear
| New York | -3.729% | 1.182% | 0.3871% | -2.18%
| Houston | -5.975% | 1.547% | 0.1695% | -4.237%
| Minneapolis | -2.516% | 0.3394% | 0.1582% | -2.019%
| Seattle | -3.906% | 2.62% | 1.407% | 0.1213%
Max Zn Damper Var Limits T&R
| New York | -0.2037% | 0.3871% | 0.1834% | 0.3667%
| Houston | -0.2542% | 0.4025% | 0.2119% | 0.4025%
| Minneapolis | -0.1121% | 0.1952% | 0.08946% | 0.1791%
| Seattle | -0.6065% | 0.9947% | 0.5337% | 0.9219%
Max Zn Damper T&R
| New York | -1.284% | 0.8557% | 0.1019% | -0.3464%
| Houston | -2.458% | 1.843% | 0% | -0.5932%
| Minneapolis | -0.8319% | 0.2903% | 0.04896% | -0.4959%
| Seattle | -0.8734% | 1.043% | 0.558% | 0.7521%
OAT Linear
| New York | -1.365% | 0.7131% | 0.4279% | -0.2241%
| Houston | 0.2542% | 0.5297% | 0.4237% | 1.208%
| Minneapolis | -1.54% | 0.2698% | 0.17% | -1.1%
| Seattle | -2.596% | 1.941% | 1.043% | 0.3882%
RAT "Bad Reset" Linear
| New York | -7.987% | 1.447% | 0.5705% | -5.97%
| Houston | -11.78% | 1.186% | 0.4661% | -10.13%
| Minneapolis | -5.692% | 0.4589% | 0.2391% | -4.994%
| Seattle | -8.079% | 3.251% | 1.674% | -3.154%
RAT Linear
| New York | -1.1% | 0.652% | 0.3056% | -0.1426%
| Houston | -1.229% | 0.678% | 0.2966% | -0.2331%
| Minneapolis | -0.6792% | 0.2615% | 0.1245% | -0.2932%
| Seattle | -1.528% | 1.528% | 0.8006% | 0.8006%
Zn Cooling − Zn Heating Linear
| New York | -1.1% | 0.1222% | 0.2852% | -0.6927%
| Houston | -0.4449% | 0.06356% | 0.2331% | -0.1483%
| Minneapolis | -0.7648% | -0.01239% | 0.08898% | -0.6882%
| Seattle | -2.086% | 1.917% | 1.067% | 0.9219%
Zn Cooling − Zn Heating T&R
| New York | -2.71% | 0.7539% | 0.3667% | -1.61%
| Houston | -2.542% | 1.208% | 0.2754% | -1.059%
| Minneapolis | -2.019% | 0.1952% | 0.1373% | -1.691%
| Seattle | -2.79% | 1.795% | 0.9461% | -0.04852%
Zn Cooling Linear
| New York | -1.345% | 0.1426% | 0.2852% | -0.9372%
| Houston | -1.208% | -0.2119% | 0.1483% | -1.229%
| Minneapolis | -0.9764% | -0.1295% | 0.08218% | -1.024%
| Seattle | -2.28% | 2.208% | 1.237% | 1.189%
Zn Cooling T&R
| New York | -2.547% | 0.978% | 0.2852% | -1.284%
| Houston | -3.284% | 1.631% | 0.1695% | -1.462%
| Minneapolis | -1.784% | 0.322% | 0.1153% | -1.354%
| Seattle | -1.82% | 1.504% | 0.8006% | 0.4609%
Zn Heating Linear
| New York | -2.017% | 0.6724% | 0.5297% | -0.8354%
| Houston | -1.208% | 0.4237% | 0.5085% | -0.2542%
| Minneapolis | -1.612% | 0.1234% | 0.1552% | -1.334%
| Seattle | -3.13% | 2.159% | 1.189% | 0.1941%
Figure 9 | EnergyPlus modeled SAT reset electricity savings breakdown by climate 8-zone commissioned
|  | Fan Savings | Cooling Savings | Pump Savings | Electricity Savings
ASHRAE Guideline 36
| New York | -0.1518% | 0.5248% | 0.6216% | 0.9946%
| Houston | 0.1666% | 0.5816% | 0.3712% | 1.119%
| Minneapolis | 0.2814% | 0.2294% | 0.2617% | 0.7725%
| Seattle | -0.2683% | 1.86% | 2.318% | 3.91%
Avg Zn Damper Linear
| New York | -0.0842% | 2.327% | 0.2055% | 2.448%
| Houston | 0.1784% | 3.666% | -0.2523% | 3.592%
| Minneapolis | 0.4197% | 1.611% | 0.04103% | 2.072%
| Seattle | -0.4267% | 3.362% | 2.691% | 5.626%
Max Zn Damper Var Limits T&R
| New York | 0.01799% | 0.5925% | 0.5892% | 1.2%
| Houston | -0.008722% | 0.6405% | 0.4459% | 1.078%
| Minneapolis | 0.0584% | 0.1871% | 0.2786% | 0.5241%
| Seattle | 0.5405% | 1.63% | 2.09% | 4.26%
Max Zn Damper T&R
| New York | 0.2803% | 2.085% | 0.02753% | 2.393%
| Houston | 1.018% | 3.148% | -0.3596% | 3.806%
| Minneapolis | 0.2233% | 1.538% | -0.06977% | 1.692%
| Seattle | 0.4071% | 2.269% | 1.807% | 4.483%
OAT Linear
| New York | -0.6248% | 0.4841% | 0.562% | 0.4213%
| Houston | -0.4317% | 0.4028% | 0.1498% | 0.1209%
| Minneapolis | -0.07953% | 0.5061% | 0.4278% | 0.8543%
| Seattle | -0.8432% | 2.671% | 2.497% | 4.324%
RAT "Bad Reset" Linear
| New York | -2.358% | 2.236% | 0.4245% | 0.3023%
| Houston | -2.263% | 3.142% | -0.2202% | 0.6587%
| Minneapolis | -1.354% | 1.311% | 0.1491% | 0.1068%
| Seattle | -2.594% | 4.015% | 3.17% | 4.592%
RAT Linear
| New York | -0.1004% | 0.7304% | 0.1031% | 0.733%
| Houston | -0.3504% | 1.843% | 0.1259% | 1.619%
| Minneapolis | 0.4728% | 0.4957% | 0.1023% | 1.071%
| Seattle | 1.199% | 1.771% | 1.565% | 4.536%
Zn Cooling − Zn Heating Linear
| New York | -0.1004% | 2.073% | 0.1207% | 2.027%
| Houston | -0.3504% | 3.622% | -0.2951% | 3.325%
| Minneapolis | 0.4728% | 1.463% | -0.05008% | 1.628%
| Seattle | 1.199% | 2.955% | 2.554% | 6.388%
Zn Cooling − Zn Heating T&R
| New York | 0.1467% | 1.698% | -0.1124% | 1.732%
| Houston | 0.2974% | 3.132% | -0.4882% | 2.941%
| Minneapolis | 0.8062% | 1.259% | -0.125% | 1.94%
| Seattle | 1.323% | 2.025% | 1.963% | 5.311%
Zn Cooling Linear
| New York | -1.43% | 2.607% | 0.3845% | 1.562%
| Houston | -1.262% | 4.007% | -0.3547% | 2.391%
| Minneapolis | -0.6165% | 1.76% | 0.05659% | 1.2%
| Seattle | -1.596% | 3.758% | 3.29% | 5.453%
Zn Cooling T&R
| New York | 0.1924% | 1.99% | 0.08225% | 2.265%
| Houston | 0.2506% | 3.37% | -0.3455% | 3.275%
| Minneapolis | 0.5742% | 1.366% | -0.04233% | 1.898%
| Seattle | 1.055% | 2.742% | 2.228% | 6.025%
Zn Heating Linear
| New York | 0.4449% | 0.4157% | 0.01616% | 0.8768%
| Houston | -0.4681% | 2.139% | 0.2671% | 1.938%
| Minneapolis | 0.8563% | 0.3212% | 0.09215% | 1.27%
| Seattle | 1.188% | 0.7499% | 1.029% | 2.967%